Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice, Fifth Edition.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers are from MasterFormat 2010 Update.

SECTION 26 05 29.15

FAST CABLE LINK SYSTEM - KINDORF®

Specifier Notes:  Delete any information below in Parts 1, 2 or 3 which is not required or relevant for the project.

PART 1 – GENERAL

1.01	SUMMARY

A.	This section includes Kindorf® fast cable link system consisting of latching connectors and wire rope assemblies for hanging support of conduit, HVAC duct, pipe, lights, cable tray, busbar, signs, etc. from  steel structures, concrete ceilings and decking.

B.	Related Sections:

1.	26 05 29.11	Modular Metal Framing System - Kindorf®

1.02	REFERENCES

A.	Underwriters Laboratories, Inc. (UL):

1.	UL-2239		Hardware for Support of Conduit, Tubing and Cable

- Canadian Standards Association (CSA)

- CSA C22.2 No. 250	Luminaries

- CSA C22.1		Canadian Electrical Code Part I (CEC)

C.	National Fire Protection Association (NFPA):

1.  	NFPA 70	 	National Electrical Code (NEC)

1.03	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:

1. Submit manufacturer’s descriptive literature and product specifications for each product.

2. Manufacturer’s product drawings.

C.	Manufacturer’s installation instructions

1.04	QUALITY ASSURANCE

A.	Manufacturer Qualifications: Products shall be free of defects in material and workmanship.

  - WARRANTY

- Product is warranted free of defects in material and workmanship.

- Product is warranted to perform the intended function within design limits.

PART 2 – PRODUCTS

2.01	GENERAL

A.	Kindorf® fast cable link system consists of the following products:

1. 	Fast Cable Link Connector

2. 	Wire Rope – two configurations:

a. 	Looped on one end

b.	Hook with safety latch on one end

- Kindorf® fast cable link system will be UL listed and CSA certified for use in support of conduit and

cable.

A.	Acceptable Manufacturers:

Thomas & Betts Corporation

8155 T&B Blvd

Memphis, TN 38125

800-816-7809, 901-252-5000

www.tnb.com

Product:	Kindorf® Fast Cable Link System

2.03	DESIGN AND PERFORMANCE REQUIREMENTS

- Kindorf® Fast Cable Link Connectors:

- Kindorf® Fast Cable Link Connectors shall be available in the following sizes.

- FCL-1, wire rope diameter 3/64” (1.2 mm)

- FCL-2, wire rope diameter 5/64” (2.0 mm)

- FCL-3, wire rope diameter 1/8” (3.2 mm)

- FCL-4, wire rope diameter 3/16” (4.8 mm)

- FCL-5, wire rope diameter 1/4” (6.4 mm)

- Kindorf® Fast Cable Link Connectors shall have the following rated load limits.

- FCL-1, 23 lb (10kg)

- FCL-2, 100 lb (45kg)

- FCL-3, 200 lb (90kg)

- FCL-4, 600 lb (272kg)

- FCL-5, 1000 lb (453kg)

- Kindorf® Fast Cable Link Connectors rated load limits shall be applicable only when used with Kindorf® Fast Cable Link wire rope.

- Kindorf® Fast Cable Link Connectors shall have a 5:1 factor of safety when used with Kindorf® Fast Cable Link wire rope with looped end.

- Kindorf® Fast Cable Link Connectors shall have a 4:1 factor of safety when used with Kindorf® Fast Cable Link wire rope with hook end.

- Kindorf® Fast Cable Link Connectors shall allow for insertion, adjustment and removal of wire rope by hand without the use of tools.

- Kindorf® Fast Cable Link Connectors shall be used in dry locations only and in environments not exceeding 200°F (93°C).

- Kindorf® Fast Cable Link Connectors shall be marked with the wire rope size and rated load limit.

- Kindorf® Fast Cable Link Wire Rope:

- Kindorf® Fast Cable Link Wire Rope shall be available with the connector in two configurations.

- Wire rope with one looped end.

- Wire rope with hook and safety latch on one end.

- Kindorf® Fast Cable Link Wire Rope shall be available with the connector in lengths of 5 ft (1.97M), 10 ft (3.94M), 15 ft (5.91M) and 30 ft (11.8M).

- Kindorf® Fast Cable Link Connectors supplied with a looped wire rope shall have a -5, -10, -15 or -30 suffix added to the catalog number indicating the wire rope length in feet.

Example: FCL-3-10

- Kindorf® Fast Cable Link Connectors supplied with a hook and safety latch wire rope shall have a -5LH, -10LH, -15LH or -30LH suffix added to the catalog number indicating the wire rope length in feet and safety latch hook.

Example: FCL-3-10LH

- Kindorf® Fast Cable Link Wire Rope shall be galvanized steel, 7 x 7 construction, unlubricated.

- Kindorf® Fast Cable Link Wire Rope with looped end shall use a zinc-plated steel compression sleeve to form the loop.

- Kindorf® Fast Cable Link Wire Rope with hook and safety latch shall have a zinc-plated forged steel hook with a with a stainless steel spring loaded latch.

PART 3 – EXECUTION

3.01	INSTALLATION

- Installation shall be in accordance with the NEC and CEC guidelines where applicable and

manufacturer’s instructions.

END OF SECTION